## Slide 2: Grid connection of distributed generation
Vesa Väisänen

## Slide 3: Requirements for power conversion
The requirements for a power conversion unit arise from three major sources:
      Fuel cell (or any other power source)
      The supplied load or network
      General requirements such as economical constraints, efficiency requirements, expected operating life, standards, patents…

## Slide 4: Load/Network requirements
There is not yet a worldwide standard available to connect distributed generation systems to the grid.
However, existing standards include references for example to responses to abnormal conditions, power quality and islanding.
The relevant standards are:
  IEEE 1547 [1]
  UL 1741 [2]
  IEC 61727 [3]
  VDE 0126-1-1 [4]
  VDE-AR-N 4105 [5]

## Slide 5: Load/Network requirements Abnormal operating conditions
Tripping (disconnection) is required, if there are too large variations in the grid frequency or voltage.
Tripping limits set by various standards, when installed power > 30 kW.

## Slide 6: Load/Network requirements Abnormal operating conditions
After the fault has been cleared, there are certain conditions under which the system can be reconnected to the grid.
The reconnection conditions have been defined for the frequency and voltage.

## Slide 7: Load/Network requirements Power quality
Power quality depends mainly on the amount of harmonic currents and DC current component.
Harmonic currents are current components that have a higher frequency than the fundamental grid frequency. The harmonic frequencies can be even or odd multipliers of the grid frequency.
Harmonic limits for Class A equipment in Europe are listed in the lower table.

## Slide 8: Load/Network requirements Power quality
In an AC network having sinusoidal waveforms the average current is ideally zero. If the average is not zero, there is a DC current component involved. The DC current can lead to saturation in the distribution transformers.
The limits for DC current injection are listed in the table below.

## Slide 9: Abnormal operating conditions Types of faults
Symmetric faults
Asymmetric faults (typical faults)
3-phase short circuit
3-phase ground fault
2-phase short circuit
1-phase (or 2-phase) ground fault

## Slide 10: Abnormal operating conditions Passive fault detection
Power flow between the power plant, load and the grid during normal operation [6]:
When the plant and the load disconnect from the grid, they are in islanding mode.
If apparent power ∆P ≠ 0 after islanding, there is a change in voltage and the voltage protection detects it.
If reactive power ∆Q ≠ 0 after islanding, there will be a phase shift in load voltage and the converters tries to compensate this by varying frequency until ∆Q = 0. The change in frequency can be detected by the frequency protection.
If ∆P and ∆Q are small, these protections may not work!

## Slide 11: Abnormal operating conditions Passive fault detection
Asymmetric faults can be detected also from the voltage vector trajectory in α-β coordinates.
During normal operation the grid voltage vector draws a circle (there is only a positive component rotating counterclockwise).
During an asymmetric fault a negative component (rotating clockwise) appears.
The sum of the positive and negative component draws an ellipse instead of a circle.
A zero component would shift the trajectory origin.
[6]

## Slide 12: Abnormal operating conditions Active fault detection
Active fault detection methods include the passive methods but also some active detection method.
For example the converter can try to sway the grid frequency and/or voltage.
If the grid frequency can be actively changed, the system is likely in an island with the load.
The method can detect islanding also in situations, where ∆P and ∆Q are small after the grid is disconnected.

## Slide 13: Abnormal operating conditions Operations during fault
Large plants need to stay connected during short duration faults.
Small plants may stay connected, if the internal protection functions allow.
In an inverter using DC link voltage control and current control there are several ways to react to a network fault:
    Immediate disconnect. Not advisable since there may be false trippings.
    Keep the DC link power constant  phase currents increase in case of voltage drop  operate until overcurrent  disconnect
    Limit the phase currents and let the DC link voltage increase  operation with a DC link brake resistor  disconnect

## Slide 14: Abnormal operating conditions Operations during fault
Grid disconnect (seen as an open circuit for the grid converter)
  Grid synchronization is lost, fault is indicated by the grid converter  inverter shutdown
  DC link voltage tends to rise  activation of DC link brake resistor
  DC/DC input current reduces due to increased DC link voltage. Current control helps to prevent overloading  DC/DC shutdown
  Fuel cell stack emergency shutdown procedures
  Voltage limiting of low voltage DC link by active or passive means.

## Slide 15: Abnormal operating conditions Operations during fault
Grid short circuit (seen as a decrease in line voltage)
  Inverter phase currents increase to maintain DC link power balance  observe the current limits and trip if necessary.
  DC/DC input current needs to be controlled to avoid overloading.
  Fuel cell stack emergency shutdown procedures, if the power conversion unit trips  voltage limiting of low voltage DC link by active or passive means

## Slide 16: Abnormal operating conditions Operations during fault
Grid converter fault (short circuit, open circuit)
  Fault is indicated by the grid converter  DC link break resistor is activated (if operational) to limit the DC link voltage.
  DC/DC input current is limited by control  shutdown
  Fuel cell emergency shutdown procedures  voltage limiting of low voltage DC link by active or passive means.

## Slide 17: Abnormal operating conditions Operations during fault
DC/DC converter fault (short circuit, open circuit)
  Fault is indicated by the DC/DC converter.
  DC link voltage tends to decrease  decrease in grid converter line currents until shutdown.
  If the DC/DC converter transistors are operational  DC/DC input current is limited by control  shutdown
  If the transistors are not operational  current cannot be limited by control  possible overloading of the fuel cell stack
  Fuel cell emergency shutdown procedures  voltage limiting of low voltage DC link by active or passive means.

## Slide 18: Abnormal operating conditions Operations during fault
Fuel cell or low voltage DC link fault (short circuit or open circuit)
  Fault is indicated by the plant controller
  DC/DC converter and the grid converter can transfer power and provide voltage limiting of low voltage DC link.
  Fuel cell emergency shutdown procedures
  Shutdown of the DC/DC and grid converter.

## Slide 19: Galvanic isolation Common-mode voltages
In a symmetrical 3-phase system the sum of phase voltages is zero.
In practice, the sum is not equal to zero  common mode voltage at the converter output terminals!
Voltage fluctuation between the output terminals and some other point (for example the negative DC-bus) causes current flow through parasitic capacitances.
Example of a non-isolated PV-system [7].
Negative DC-bus
Common-mode current path

## Slide 20: Galvanic isolation Common-mode voltages
In case of galvanic isolation the common-mode current route is blocked.
Only route is through the transformer capacitances, which are typically small  even large voltage variations cause only small leakage currents.
Example of an isolated PV-system [7].
Transformer capacitances

## Slide 21: Galvanic isolation Other advantages
The voltage levels between different systems can be adjusted by the transformer turns ratio.
A transformer isolates the power plant galvanically from the grid, thus isolating any line or ground faults to the faulty side.
If the ground potentials of two systems are connected together and if there is any voltage difference between the ground potentials, there will be a large DC current (limited by the small cable resistance). A transformer will isolate the ground potentials and block any DC currents from flowing.

## Slide 22: Summary
Standards and grid codes need to be taken into account when connecting distributed generation to the grid.
Faults can be detected by passive and active methods. Both methods require measurements of current, voltage and frequency.
The only uncontrollable power electronics fault in terms of power plant current limiting is a DC/DC converter fault, where some the primary transistors or the input capacitors are short circuited.
Galvanic isolation is used to limit ground currents, to provide voltage conversion and to provide safety during fault situations.

## Slide 23: References
[1] IEEE Std 1541-2003, IEEE Standard for Interconnecting Distributed Resources With Electric Power Systems, 1547, The Institute of Electrical and Electronics Engineers, Inc. New York, USA.
[2] Underwriters Laboratories Inc (2001), UL741 Inverters, Converters, and Controllers for Use in Independent Power Systems, 741, Underwriters Laboratories Inc. (UL), IL, USA.
[3] IEC (2004), IEC 61727 Ed. 2, Photovoltaic (PV) Systems - Characteristics of the Utility Interface, 61727,
International Electrotechnical Commission (IEC), Geneva, Switzerland.
[4] VDE Verlag (2006), Automatic Disconnection Device between a Generator and the Public Low-Voltage
Grid, 0126-1-1, VDE VERLAG GMBH, Berlin-Offenbach.
[5] VDE-AR-N 4105 (2011), Generators connected to the low-voltage distribution network - Technical requirements for the connection to and parallel operation with low-voltage distribution networks.
[6] Purhonen, M. (2009). Verkkovaihtosuuntaajan säätö verkon erikoistilanteissa polttokennosovelluksissa. M.Sc. Thesis. Lappeenranta University of Technology, Finland.
[7] Kerekes, T., Teodorescu, R., and Liserre, M. (2008). Common mode voltage in case of transformerless PV inverters connected to the grid. In: IEEE International Symposium on Industrial Electronics. pp. 2390-2395.

## Slide 24: Thank you! Any questions?